## Current Transformer
| Outdoor Current Transformer | 69kV Current Transformer | 115kV Current Transformer | 230kV Current Transformer | 345kV Current Transformer | Bidder's Response Please fill all fields marked Orange
| Technical Tender Form |  | Rattlesnake and Sun Ranch 115kV Substations
Please provide the following information with your bid.
1 | Manufacurer/Supplier Information
2 | Name of Manufacturer | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
3 | Name of Supplier/Agent | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
4 | Name and contact information of Manufacturer’s person to be single point of contact with PNM | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
5 | Bidders Tender Reference Number | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
6 | Manufacturing location | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
7 | The CTs will be supplied in accordance with PNM Current Transformer General Specification # SE-CT-2023 | Yes | Yes | Yes | Yes
8 | Number of CTs to be supplied | Project Specific | Nine (9) | Project Specific | Project Specific
9 | Delivery time from PO Award (weeks) | Bidder to confirm | Bidder to confirm | Bidder to confirm | Bidder to confirm
10 | Method of shipment | Bidder to confirm (Rail shipping not preferred) | Bidder to confirm (Rail shipping not preferred) | Bidder to confirm (Rail shipping not preferred) | Bidder to confirm (Rail shipping not preferred)
11 | Current Transformer Type | Inductive | Inductive | Inductive | Inductive
12 | System Characteristics
13 | PNM Nominal Voltage Classification (Phase-to-phase RMS, kV) | 69 | 115 | 230 | 345
14 | Maximum System Voltage (Phase-to-phase RMS, kV) | 79.6 | 123 | 245 | 380
15 | Frequency (Hz) | 60 | 60 | 60 | 60
16 | Type of System Grounding | Effectively Grounded | Effectively Grounded | Effectively Grounded | Effectively Grounded
17 | Method of System Grounding | Neutral Solidly Grounded | Neutral Solidly Grounded | Neutral Solidly Grounded | Neutral Solidly Grounded
18 | First Pole to Clear Factor | 1.5 | 1.5 | 1.5 | 1.5
19 | Maximum System 3 phase short-circuit current, symmetrical (kA) | (Project Specific) | 63 | (Project Specific) | (Project Specific)
20 | Installation Environment
21 | Installation Location | Outdoor | Outdoor | Outdoor | Outdoor
22 | Elevation Above sea level (ft) | 3300' to 7300' (Project specific) | 7300' | 3300' to 7300' (Project specific) | 3300' to 7300' (Project specific)
23 | Ambient Air Temperature (°C)
24 | a) Maximum | 40 | 40 | 40 | 40
25 | b) Max. for 6 hours | 50 | 50 | 50 | 50
26 | c) Minimum | -40 | -40 | -40 | -40
27 | Maximum Wind velocity (ft/s) | 40 | 40 | 40 | 40
28 | Maximum Ice Build-up (in) | 20 | 20 | 20 | 20
29 | Seismic Earthquake Degree | IEEE 693 "Moderate Seismic Level" | IEEE 693 "Moderate Seismic Level" | IEEE 693 "Moderate Seismic Level" | IEEE 693 "Moderate Seismic Level"
30 | Ambient Sunlight Exposure - solar radiation level | New Mexico Continuous current based on IEEE C37.24, Fig A.2 | New Mexico Continuous current based on IEEE C37.24, Fig A.2 | New Mexico Continuous current based on IEEE C37.24, Fig A.2 | New Mexico Continuous current based on IEEE C37.24, Fig A.2
31 | Lightning Ground flash density | Per IEEE 998 (New Mexico) | Per IEEE 998 (New Mexico) | Per IEEE 998 (New Mexico) | Per IEEE 998 (New Mexico)
32 | Min. Creepage Distance (mm/kV @ max. equipmet voltage ph-gnd) | 54 (Extra heavy, IEEE C57.13.5) | 54 (Extra heavy, IEEE C57.13.5) | 54 (Extra heavy, IEEE C57.13.5) | 54 (Extra heavy, IEEE C57.13.5)
33 | Equipment Technical Data
34 | Equipment type and designation | Enter Manufacturer's Breaker Type and Designation | Enter Manufacturer's Breaker Type and Designation | Enter Manufacturer's Breaker Type and Designation | Enter Manufacturer's Breaker Type and Designation
35 | National/International Standards utilized (with dates) | Enter main governing standards (IEEE) | Enter main governing standards (IEEE) | Enter main governing standards (IEEE) | Enter main governing standards (IEEE)
36 | List of all type tests conducted (with dates of test) in accordance with identified National and International Standards utilized to validate each rating: | Type tests mainly per IEEE C57.13.5 | Type tests mainly per IEEE C57.13.5 | Type tests mainly per IEEE C57.13.5 | Type tests mainly per IEEE C57.13.5
37 | Rated frequency(Hz) | 60 | 60 | 60 | 60
38 | Rated Nominal Equipment Voltage(kV, rms) | 69 | 115 | 230 | 345
39 | Rated Maximum Equipment Voltage(kV, rms) | 79.6 | 123 | 245 | 380
40 | Rated Insulation Levels
41 | a) Lightning impulse withstand voltage
42 | i) Full wave (1.2 X 50 ms) (kV Crest) | 350 | 550 | 1050 | 1300
43 | ii) Chopped wave (TTF = 3 ms ) (kV Crest) | 400 | 630 | 1210 | 1500
44 | b) Power frequency withstand voltage
45 | i) One minute, dry (kV, rms) | 140 | 230 | 460 | 575
46 | ii) Ten second, wet (kV, rms) | 140 | 230 | 460 | N/A
47 | iii) One minute, dry on secondary windings (kV rms) | 3 | 3 | 3 | 3
48 | c) Switching impulse withstand voltage (kV Crest) | N/A | N/A | N/A | 975
49 | Rated Voltages
50 | Continuous current rating factor (RF)
51 | a) Primary | Project Specific | 1 | Project Specific | Project Specific
52 | a) Secondary | Project Specific | 4 | Project Specific | Project Specific
53 | Short time (1 sec.) thermal current rating (kA) | 40 | 40 | 40 | 40
54 | Accuracy rating primary voltage (V, rms, Ph-Gnd) | 69000 (Line to line) | 69000 | 138000 | 207000
55 | Maximum internal discharge (___ pc at ___ kV rms, ph-gnd) | 10 at 82.8 | 10 at 123 | 10 at 245 | 10 at 362
56 | Maximum external RIV (___ µV at ___ kV rms extinction voltage) | N/A | N/A | <250 at 156 | <250 at 230
57 | Maximum power factor/dissipation factor @ rated voltage and 20o C (%) | <0.5% | <0.5% | <0.5% | <0.5%
58 | Maximum power factor/dissipation factor @ 10 kV (rms) and 20o C (%) | <0.5% | <0.5% | <0.5% | <0.5%
59 | The CT can be energized at temperatures down to (°C) | -40 | -40 | -40 | -40
60 | The CT can be operated at temperatures down to (°C) | -40 | -40 | -40 | -40
61 | Physical Attributes
62 | Overall height (in) | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
63 | Height between base to terminal (in) | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
64 | Creepage distance of external insulation (minimum, mm) | 2260 | 3840 | 7640 | 11290
65 | Degree of protection provided by enclosures (Ipxx and/or NEMA rating) | NEMA 4 | NEMA 4 | NEMA 4 | NEMA 4
66 | Insulation contamination level | Heavy | Heavy | Heavy | Heavy
67 | Insulation Technology | Oil | Oil | Oil | Oil
68 | Total weight of complete transformer (kg) | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
69 | Maximum terminal loading (any direction)(Static/Dynamic) (kN) | 2.0/1.4*Static | 2.0/1.4*Static | 2.5/1.4*Static | 2.5/1.4*Static
70 | Internal Arc Protection Class | Class 1 | Class 1 | Class 1 | Class 1
71 | Characteristics of Protection of Secondary Windings
72 | Number of Secondary Cores | 1 | 1 | 1 | 1
73 | Core Number. (ie W,X ,Z etc) | Z | Z | Z | Z
74 | Secondary Connection (1-5)
75 | Ratio ( to 5 A) | Project Specific | Project Specific | Project Specific | Project Specific
76 | Protection Accuracy | C800 | C800 | C800 | C800
77 | Secondary Connection (2-4)
78 | Ratio ( to 5 A) | Project Specific | Project Specific | Project Specific | Project Specific
79 | Protection Accuracy | C800 | C800 | C800 | C800
80 | Secondary Connection (1-2)
81 | Ratio ( to 5 A) | Project Specific | Project Specific | Project Specific | Project Specific
82 | Protection Accuracy | C800 | C800 | C800 | C800
83 | Characteristics of Protection and Metering of Secondary Windings
84 | Core Number. (ie Y etc) | Z | Z | Z | Z
85 | Secondary Connection (1-5) |  | NA
86 | Ratio ( to 5 A) | Project Specific |  | Project Specific | Project Specific
87 | Protection Accuracy | C800 |  | C800 | C800
88 | Metering Accuracy | Project Specific |  | Project Specific | Project Specific
89 | Secondary Connection (2-4) |  | NA
90 | Ratio ( to 5 A) | Project Specific |  | Project Specific | Project Specific
91 | Protection Accuracy | C800 |  | C800 | C800
92 | Metering Accuracy | Project Specific |  | Project Specific | Project Specific
93 | Secondary Connection (1-2) |  | Single Ratio -- 400% to 0.05%
94 | Thermal Rating Factor |  | 4
94 | Ratio ( to 5 A) | Project Specific | 300 | Project Specific | Project Specific
95 | Protection Accuracy | C800 | 0.15B1.8 | C800 | C800
96 | Metering Accuracy | Project Specific | 0.15B1.8 | Project Specific | Project Specific
97 | Primary, Secondary and Grounding Terminals
98 | Primary (High Voltage) Terminals
99 | Bolt pattern per NEMA CC1 | 4 Hole NEMA Pad | 4 Hole NEMA Pad | 4 Hole NEMA Pad / 6 Hole NEMA Pad | 4 Hole NEMA Pad / 6 Hole NEMA Pad
100 | Terminal Material | Aluminum | Aluminum | Aluminum | Aluminum
101 | List bi-metallic plating (if any) | Silver (reqd for stud, otherwise optional) | Silver (reqd for stud, otherwise optional) | Silver (reqd for stud, otherwise optional) | Silver (reqd for stud, otherwise optional)
102 | Corona or Grading Rings Provided (Yes/No) | As Reqd. | As Reqd. | As Reqd. | As Reqd.
103 | Secondary (Low Voltage) Terminals
104 | Secondary Terminal Type | Threaded Stud (6mm dia)/ Terminal Blocks (single screw clamp type from Wieland/Phoenix) | Threaded Stud (6mm dia)/ Terminal Blocks (single screw clamp type from Wieland/Phoenix) | Threaded Stud (6mm dia)/ Terminal Blocks (single screw clamp type from Wieland/Phoenix) | Threaded Stud (6mm dia)/ Terminal Blocks (single screw clamp type from Wieland/Phoenix)
105 | Terminal Box Protection class (NEMA or IPxx) | NEMA 4 | NEMA 4 | NEMA 4 | NEMA 4
106 | Secondary Wire Size (AWG) | #8 to #14 | #8 to #14 | #8 to #14 | #8 to #14
107 | Grounding Terminal (inside secondary terminal box) | Lug (#10 to #14) | Lug (#10 to #14) | Lug (#6 to #10) | Lug (#6 to #10)
108 | Grounding Terminal Connector/Pad | Can accommodate 2/0 AWG to 350 MCM Cu OR 2 Hole NEMA Pad | Can accommodate 2/0 AWG to 350 MCM Cu OR 2 Hole NEMA Pad | Can accommodate 2/0 AWG to 350 MCM Cu OR 2 Hole NEMA Pad | Can accommodate 2/0 AWG to 350 MCM Cu OR 2 Hole NEMA Pad
109 | Anti Condensation heater provided, if required (Yes/No) | Yes (Required) | Yes (Required) | Yes (Required) | Yes (Required)
110 | Voltage supply for anti condensation heater (V, rms) | 120 (Single phase) | 120 (Single phase) | 120 (Single phase) | 120 (Single phase)
111 | Oil Insulation
112 | Manufacturer trade name for oil used in the Current Transformer | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
113 | Certified PCB free (shall be stamped on the nameplate) | Yes | Yes | Yes | Yes
114 | Type of temperature expansion mechanism | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
115 | Manufacturer trade name for oil used | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
116 | Has mechanical and sealing endurance testing been done according to specifications? | Yes | Yes | Yes | Yes
117 | External Insulator
118 | Type of Hollow Insulator (i.e., Porcelain, Composite with SiR Sheds) | Composite (preferred) Porcelain | Composite (preferred) Porcelain | Composite (preferred) Porcelain | Composite (preferred) Porcelain
119 | Material composition of composite insulator and SiR sheds | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
120 | Manufacturing process of SiR sheds | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
121 | Manufacturing process of Porcelain sheds | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
122 | Insulator subsupplier name and manufacturing plant location | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
123 | Type tests provided? | Yes (Required) | Yes (Required) | Yes (Required) | Yes (Required)
124 | External finish | ANSI Grey No. 70 | ANSI Grey No. 70 | ANSI Grey No. 70 | ANSI Grey No. 70
125 | Spare Parts
126 | Identify commissioning and startup spare parts | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
127 | Identify spare parts required in the first five years of operation | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
128 | Provide replacement schedule and criteria for limited-life parts | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
129 | Identify special tools for installation and commissioning | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
130 | Identify special tools for maintenance | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
131 | Exceptions and Additional Information
132 | List of all exceptions to PNM's specification with relavent section numbers. If no, state "full compliance"(vendor is responsible for confirming if proposed product fully complies with the requirements of the stated spec). Provide signed document confirming compliance. | Confirm full compliance | Confirm full compliance | Confirm full compliance | Confirm full compliance
133 | Drawings available for review after PO (weeks) | Vendor to confirm | Vendor to confirm | Vendor to confirm | Vendor to confirm
134 | CAD drawings to be provided during approval stage | Yes (Required) | Yes (Required) | Yes (Required) | Yes (Required)
135 | 3D Model to be provided during approval stage | (Project Specific) | (Project Specific) | (Project Specific) | (Project Specific)
136 | List of supplemnetary docs provided with bid
137 | Drawings (Outline, nameplates, secondary terminal box etc.) | Required | Required | Required | Required
138 | Excitation Curves | Required | Required | Required | Required
139 | Type test results and certificates provided with bid | Required to be submitted for technical evaluation during bid stage | Required to be submitted for technical evaluation during bid stage | Required to be submitted for technical evaluation during bid stage | Required to be submitted for technical evaluation during bid stage
140 | List of routine tests to be performed on each unit (ITP) | List required | List required | List required | List required
141 | Field assembly and installation requirements | Provide documentation with bid | Provide documentation with bid | Provide documentation with bid | Provide documentation with bid
142 | Special instructions for storage and handling | Provide documentation with bid | Provide documentation with bid | Provide documentation with bid | Provide documentation with bid
143 | List of additional type tests to be performed as part of this order | If type tests are missing per PNM spec, vendor to confirm plan for completing type tests along with costs and lead time | If type tests are missing per PNM spec, vendor to confirm plan for completing type tests along with costs and lead time | If type tests are missing per PNM spec, vendor to confirm plan for completing type tests along with costs and lead time | If type tests are missing per PNM spec, vendor to confirm plan for completing type tests along with costs and lead time
144 | Field services included in bid price (as applicable) | Vendor to state | Vendor to state | Vendor to state | Vendor to state